{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["Temp. Max Equip. PLC","Temp. Max Equip. Exd"],"not_rendered":{"macros":1,"external_links":1,"defined_names":45},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Temp. Max Equip. PLC","index":0,"n_rows":26,"n_cols":10,"rows_kept":26,"hidden":true,"merged":[[14,4,14,9]],"flags":["formulas_cached_only"]}
[]
[null,null,"Température"]
[null,null,"maximum external temperature (Te max)",{"v":45,"d":"45 °c"}]
[null,null,"maximal internal temperature (Ti max)",{"v":55,"d":"55 °c"}]
[null,null,"Altitude ( f )",3.1]
[]
[null,null,"Electrical data"]
[null,null,"Ventilation nominal voltage","24 V"]
[]
[null,null,"Enveloppe"]
[null,null,"Cubicle type"]
[null,null,"Dimension H (mm)",{"v":680,"d":"680 mm"}]
[null,null,"Dimension W (mm)",{"v":640,"d":"640 mm"}]
[null,null,"Dimension D (mm)",{"v":400,"d":"400 mm"}]
[null,null,"Matérial (K)",{"v":12,"d":"12.0 W/m².°c"},"painted aluminium"]
[null,null,"Disposition (Free side)",null,"Top","Bott","Left","Right","Behind","front"]
[null,null,"1 = free face",null,1,1,1,1,1,1]
[null,null,"Cubicle Total surface",{"v":1.9264,"d":"1.93 m²"}]
[]
[null,null,"CALCUL"]
[null,null,"Corrected disposition Cubicle surface (S / free side)",{"v":1.9264,"d":"1.93 m²"}]
[null,null,"Total power to be dissipated (Pd)",{"$error":"#REF!"}]
[null,null,"Cubicle natural dissipated power (Pc=K x S x (Ti-Te))",{"v":231.16799999999998,"d":"231 W"}]
[null,null,"Power to be dissipated (Psyst=Pd-Pc)",{"$error":"#REF!"}]
[null,null,"Minimum Fan flow (F=f x Psyst / (Ti - Te)",{"$error":"#REF!"}]
[null,null,"delta t without fan dt(Ti-Te)= Pd / (K x S)",{"$error":"#REF!"}]

{"sheet":"Temp. Max Equip. Exd","index":1,"n_rows":62,"n_cols":29,"rows_kept":62,"merged":[[0,18,0,20],[0,22,0,28],[1,7,1,12],[2,7,2,9],[2,10,2,12],[19,3,19,5],[22,4,22,6],[22,7,22,8],[22,9,23,9],[22,10,22,11],[22,12,23,12],[22,13,23,13],[30,7,30,8],[30,10,30,11],[36,4,37,4],[36,5,37,5],[36,8,38,8],[37,14,37,16]],"flags":["formulas_cached_only"]}
[{"$nulls":18},"Autre méthode de calcule",{"$nulls":3},"Données"]
[null,null,"Température","°C","°K",null,null,"Convection Naturelle"]
[null,null,"Temperature externe maximale (Te max)",{"v":45,"d":"45 °c"},318.15,null,null,"Intérieure",null,null,"Extérieure",{"$nulls":7},"H conv 2","Laminaire","Turbulent",null,"Fluide","ρ","µ","Cp","λ","β","Pr"]
[null,null,"Temperature externe maximale (Te min)",{"v":-5,"d":"-5 °c"},268.15,null,null,"Gr","Pr","Ra (Gr*Pr)","Gr","Pr","Ra (Gr*Pr)",{"$nulls":5},"Verticale",{"v":2.5925534388577858,"d":"2.6 W/m².°c"},{"v":2.92319054869214,"d":"2.9 W/m².°c"},null,null,"kg/m3","Pl","J/kg/°C","W/m/°C","m3/m3/°C"]
[null,null,"Temperature interne maximale (Ti max)",{"v":55,"d":"55 °c"},328.15,null,"Horizontale",{"v":314100190.4654867,"d":"3.14E+08"},0.707,{"v":222068834.6590991,"d":"2.22E+08"},{"v":430864458.8003932,"d":"4.31E+08"},0.707,{"v":304621172.37187797,"d":"3.05E+08"},{"$nulls":5},"Horizontale",{"v":2.4099792530227306,"d":"2.4 W/m².°c"},{"v":2.7751276246928414,"d":"2.8 W/m².°c"},null,"Air à 0°C et Patm",1.284,1.7250000000000003e-05,"1,004.103",0.024,0.00367,0.715]
[null,null,"Altitude ( f )",3.1,null,null,"Verticale",{"v":1182292074.948279,"d":"1.18E+09"},0.707,{"v":835880496.9884331,"d":"8.36E+08"},{"v":1454167548.451327,"d":"1.45E+09"},0.707,{"v":1028096456.7550882,"d":"1.03E+09"}]
[{"$nulls":18},"H conv 3",{"v":2.4208585681696744,"d":"2.4 W/m².°c"},null,null,"Couleur"," DeltaT [ºC]","Coef absorbsion"]
[null,null,"Données Electrique",{"$nulls":4},"Nu","Laminaire","Turbulant","Nu","Laminaire","Turbulant",{"$nulls":9},"Blanc",4,{"v":0.1306878306878307,"d":"13%"}]
[null,null,"Tension Nominale Ventilation","24 V",{"$nulls":3},"Haut",{"v":91.81841845235327,"d":"92"},{"v":123.15034111285797,"d":"123"},"Haut",{"v":96.6946009442728,"d":"97"},{"v":131.85579156366475,"d":"132"},{"$nulls":9},"Beige",7,{"v":0.2287037037037037,"d":"23%"}]
[null,null,"Débit ventilateur intérieure",{"v":5,"d":"0 m/s"},{"$nulls":3},"Bas",42.50852706127466,"//","Bas",44.76601895568185,"//",{"$nulls":9},"Jaune",9,{"v":0.29404761904761906,"d":"29%"}]
[{"$nulls":7},"Verticale",{"v":100.50996260699173,"d":"101"},{"v":136.93245105297726,"d":"137"},"Verticale",{"v":105.8116125813463,"d":"106"},{"v":146.0127149941437,"d":"146"},{"$nulls":9},"Gris clair",14,{"v":0.4574074074074074,"d":"46%"}]
[null,null,"Enveloppe Exd",{"$nulls":19},"Gris",22,{"v":0.7187830687830687,"d":"72%"}]
[null,null,"Type de Coffret",{"$nulls":4},"H conv","Laminaire","Turbulant","H complexe","Laminaire","Turbulant",{"$nulls":9},"Sombre",25,{"v":0.8167989417989419,"d":"82%"}]
[null,null,"Fabricant",{"$nulls":4},"Haut",{"v":4.0808185978823674,"d":"4.1 W/m².°c"},{"v":5.4733484939047985,"d":"5.5 W/m².°c"},"Haut",{"v":3.8677840377709125,"d":"3.9 W/m².°c"},{"v":5.27423166254659,"d":"5.3 W/m².°c"},{"$nulls":9},"Noir",27,{"v":0.8821428571428571,"d":"88%"}]
[{"$nulls":3},"Constructeur","Extérieure","Intérieure",null,"Bas",{"v":1.8892678693899847,"d":"1.9 W/m².°c"},{"v":1.8892678693899847,"d":"1.9 W/m².°c"},"Bas",{"v":1.790640758227274,"d":"1.8 W/m².°c"},{"v":1.790640758227274,"d":"1.8 W/m².°c"},{"$nulls":9},"Aluminum / acier inox",14,{"v":0.4574074074074074,"d":"46%"}]
[null,null,"Hauteur H (mm)",{"v":960,"d":"960 mm"},{"v":900,"d":"900 mm"},{"v":840,"d":"840 mm"},null,"Verticale",{"v":2.8717132173426214,"d":"2.9 W/m².°c"},{"v":3.912355744370779,"d":"3.9 W/m².°c"},"Verticale",{"v":2.821643002169235,"d":"2.8 W/m².°c"},{"v":3.893672399843832,"d":"3.9 W/m².°c"}]
[null,null,"Largeur L (mm)",{"v":660,"d":"660 mm"},{"v":600,"d":"600 mm"},{"v":540,"d":"540 mm"},{"$nulls":16},"Matière","Rho","H"]
[null,null,"Profondeur P (mm)",{"v":460,"d":"460 mm"},{"v":460,"d":"460 mm"},{"v":400,"d":"400 mm"},{"$nulls":16},"sheet steel",45,{"v":5.5,"d":"5.5 W/m².°c"}]
[null,null,"Epaisseur (mm)",{"v":30,"d":"30 mm"},{"v":30,"d":"30 mm"},{"v":30,"d":"30 mm"},"rho","Soleil?","Couleur","Orientation","H estimé",null,"H cond",{"v":6.78,"d":"6.8 W/m².°c"},{"$nulls":8},"polyester",0.42,{"v":3.5,"d":"3.5 W/m².°c"}]
[null,null,"Matiere (K)","aluminium",null,null,226,"Non","Gris clair","Sud",{"v":12,"d":"12.0 W/m².°c"},null,"H rad",{"v":2.3462622243174778,"d":"2.3 W/m².°c"},{"$nulls":8},"aluminium",226,{"v":12,"d":"12.0 W/m².°c"}]
[{"$nulls":8},{"v":0.4574074074074074,"d":"46%"},{"v":0.36800000000000005,"d":"0.37 m²"},{"$nulls":12},"stainless steel",0.42,{"v":6.5,"d":"6.5 W/m².°c"}]
[]
[{"$nulls":4},"Données",null,null,"Convection intérieure",null,"Conduction","Convection extérieure",null,"Radiation","Total"]
[{"$nulls":4},"Surface ext","Surface int","Coef","H conv int","Conv int",null,"H conv ext","Conv ext"]
[{"$nulls":3},"Haut",{"v":0.276,"d":"0.276 m²"},{"v":0.216,"d":"0.216 m²"},0.75,{"v":4.0808185978823674,"d":"4.1 W/m².°c"},{"v":0.6610926128569435,"d":"0.7 W/°c"},{"v":1.46448,"d":"1.5 W/°c"},{"v":3.8677840377709125,"d":"3.9 W/m².°c"},{"v":0.8006312958185788,"d":"0.8 W/°c"},{"v":0.6475683739116239,"d":"0.6 W/°c"},{"v":2.1092922825871465,"d":"2.1 W/°c"}]
[{"$nulls":3},"Bas",{"v":0.276,"d":"0.276 m²"},{"v":0.216,"d":"0.216 m²"},{"v":1,"d":"1.00"},{"v":1.8892678693899847,"d":"1.9 W/m².°c"},{"v":0.4080818597882367,"d":"0.4 W/°c"},{"v":1.46448,"d":"1.5 W/°c"},{"v":1.790640758227274,"d":"1.8 W/m².°c"},{"v":0.4942168492707277,"d":"0.5 W/°c"},{"v":0.6475683739116239,"d":"0.6 W/°c"},{"v":1.5498670829705883,"d":"1.5 W/°c"}]
[{"$nulls":3},"Gauche",{"v":0.414,"d":"0.414 m²"},{"v":0.336,"d":"0.336 m²"},{"v":1,"d":"1.00"},{"v":2.8717132173426214,"d":"2.9 W/m².°c"},{"v":0.9648956410271209,"d":"1.0 W/°c"},{"v":2.27808,"d":"2.3 W/°c"},{"v":3.893672399843832,"d":"3.9 W/m².°c"},{"v":1.6119803735353464,"d":"1.6 W/°c"},{"v":0.9713525608674357,"d":"1.0 W/°c"},{"v":3.5482285754299028,"d":"3.5 W/°c"}]
[{"$nulls":3},"Droite",{"v":0.414,"d":"0.414 m²"},{"v":0.336,"d":"0.336 m²"},{"v":1,"d":"1.00"},{"v":2.8717132173426214,"d":"2.9 W/m².°c"},{"v":0.9648956410271209,"d":"1.0 W/°c"},{"v":2.27808,"d":"2.3 W/°c"},{"v":3.893672399843832,"d":"3.9 W/m².°c"},{"v":1.6119803735353464,"d":"1.6 W/°c"},{"v":0.9713525608674357,"d":"1.0 W/°c"},{"v":3.5482285754299028,"d":"3.5 W/°c"}]
[{"$nulls":3},"Arriere",{"v":0.54,"d":"0.540 m²"},{"v":0.4536,"d":"0.454 m²"},0.75,{"v":2.8717132173426214,"d":"2.9 W/m².°c"},{"v":0.9769568365399598,"d":"1.0 W/°c"},{"v":3.075408,"d":"3.1 W/°c"},{"v":3.893672399843832,"d":"3.9 W/m².°c"},{"v":1.576937321936752,"d":"1.6 W/°c"},{"v":1.266981601131438,"d":"1.3 W/°c"},{"v":3.8208757596081497,"d":"3.8 W/°c"}]
[{"$nulls":3},"Devant",{"v":0.54,"d":"0.540 m²"},{"v":0.4536,"d":"0.454 m²"},{"v":1,"d":"1.00"},{"v":2.8717132173426214,"d":"2.9 W/m².°c"},{"v":1.302609115386613,"d":"1.3 W/°c"},{"v":3.075408,"d":"3.1 W/°c"},{"v":3.893672399843832,"d":"3.9 W/m².°c"},{"v":2.1025830959156693,"d":"2.1 W/°c"},{"v":1.266981601131438,"d":"1.3 W/°c"},{"v":4.67217381243372,"d":"4.7 W/°c"}]
[{"$nulls":3},"Total",{"v":2.46,"d":"2.460 m²"},{"v":2.0112,"d":"2.011 m²"},null,{"v":5.278531706625995,"d":"5.3 W/°c"},null,{"v":13.635936,"d":"13.6 W/°c"},{"v":8.19832931001242,"d":"8.2 W/°c"},null,{"v":5.771805071820996,"d":"5.8 W/°c"},{"v":32.88460208845941,"d":"32.9 W/°c"}]
[]
[null,null,"CALCUL"]
[null,null,"Surface corrigée du Coffret ( S/ Coté libre)",null,{"v":2.8686,"d":"2.87 m²"}]
[null,null,"Puissance Totale Dissipée (Pd)",null,{"v":176,"d":"176 W"}]
[]
[{"$nulls":4},"T amb","T Objectif","Méthode 1","Méthode 2","Puissance résistance sup"]
[null,null,"Delta Temperature sans Ventilation dt=Pd/(KxS)",{"$nulls":3},{"v":5.1128308814985255,"d":"5.11 °c"},{"v":5.35204894760657,"d":"5.35 °c"},{"$nulls":3},"Ensoleillement","W/m²/j",null,"Exposition soleil",{"$nulls":3},"Energie soleil"]
[null,null,"Temperature Interne Maximale Calculée (Tic max=Te max+Dt)",null,{"v":45,"d":"45 °c"},{"v":55,"d":"55 °c"},{"v":50.112830881498525,"d":"50.11 °c"},{"v":50.35204894760657,"d":"50.35 °c"},{"$nulls":3},"Min",2270,null,"Orientation","Sans carter","Avec carter",null,{"v":0,"d":".0 W"}]
[null,null,"Temperature Interne Minimale Calculée (Tic min=Te min+Dt)",null,{"v":-5,"d":"-5 °c"},{"v":10,"d":"10 °c"},{"v":0.11283088149852549,"d":"0.11 °c"},{"v":0.35204894760657,"d":"0.35 °c"},{"v":317.2690313268912,"d":"317.3 W"},null,null,"Max",7640,null,"Nord",{"v":0.22999999999999998,"d":"0.230 m²"},{"v":0,"d":"0.000 m²"},null,{"v":0,"d":".0 W"}]
[{"$nulls":14},"Est",{"v":0.27199999999999996,"d":"0.272 m²"},{"v":0,"d":"0.000 m²"}]
[{"$nulls":14},"Sud",{"v":0.36800000000000005,"d":"0.368 m²"},{"v":0,"d":"0.000 m²"}]
[{"$nulls":14},"Ouest",{"v":0.27199999999999996,"d":"0.272 m²"},{"v":0,"d":"0.000 m²"}]
[]
[null,null,"http://forums.futura-sciences.com/habitat-bioclimatique-isolation-chauffage/191859-calcul-de-temperature-interieure.html"]
[null,null,"http://automatuto.com/gestion-thermique/"]
[null,null,"http://processs.free.fr/Pages/VersionMobile0.php?page=4500"]
[]
[]
[]
[]
[]
[null,null,"Disposition (selectionner A1 à A7)","A1",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"}]
[null,null,"Surface Totale du Coffret (T+B+L+R+B+F)",{"v":2.46,"d":"2.46 m²"},{"v":1,"d":"1.00"},{"v":0.7,"d":"0.70"},{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},1.15,{"v":1.3,"d":"1.30"}]
[null,null,"POSITION"]
[null,"A1","Toutes les faces libres","A1","A1"]
[null,"A2","Adossé au mur","A2",{"$nulls":4},"A2"]
[null,"A3","Extremité","A3","A3",null,"A3"]
[null,"A4","Extremité, Adossé au mur","A4",{"$nulls":3},"A4",null,"A4"]
[null,"A5","Milieu","A5",null,"A5"]
[null,"A6","Milieu, Adossé au mur","A6",{"$nulls":4},"A6"]
[null,"A7","Milieu, Adossé au mur, Toit Couvert","A7",null,"A7"]